## Overview
BZ172Lab
<brief description here>
Author | BoTong ZHANG (SESA198459)
Contact | botong.zhang@se.com
Revision | 1.1
Last Modification | 2021-02-22

## Change Log
Date | History
2021-01-06 | Created by BZ
2021-01-12 | Update I/O map by adding evap coil outlet pressure sensor
2021-01-25 | 1.0 version
2021-02-10 | 1.1 version

## Track
2021-02-22
Must | 136
Optional | 7
Nice to have | 5
Deprecated | 0
148
Planning | 4
Pending Approval | 10
Approved | 42
In Progress | 9
Pending Review | 0
On Hold | 1
Completed | 82
Deliverables |  | Requirement Status
Date | Revision | Planning | Approved | Pending Approval | In Progress | Completed
2021-01-25 | 1.0 | 8 | 108 | 11 | 0 | 0
2021-02-10 | 1.1 | 9 | 59 | 10 | 7 | 56
2021-03-01 | 1.2

## Requirements
ID | LEVEL | STATUS | REQUIREMENT | COMMENT
GF |  |  | Generic Functions
GF.001 | Must | Approved | The application should have two working modes, real and simulation. √ Real mode All the functions are implemented by the real hardwares, for example, the readings are from sensors and the outputs are set to the actuators. This is the default mode when the controller is powered up. √ Simulation mode The control related functions are exactly identical to the real mode except the inputs and outputs from the sensors and actuators are redirected to the data items. (Refer to MB-map)
GF.002 | Must | Completed | The transition between real and simulation mode is triggered by selecting the mode from the small local screen on the controller. When the controller is powered up, the default mode 'REAL' is showed up on the local screen. Long-pressing of the 'Enter' button is to toggle the controller mode.
GF.003 | Nice to have | Approved | Simulation mode is not available on the formal release version.
GF.004 | Must | Approved | The configuration items saved in EEPROM can be reset to defaults by a modbus register. (Refer to MB-map)
GF.005 | Must | In Progress | All MB data are exposed through one of RS485 ports from the controller. (Refer to Modbus Register Map)
GF.006 | Nice to have | Planning | Some status variables can be recorded into the microSD card
GF.007 | Must | Completed | Inputs and outputs should follow M172 IO map
GF.008 | Must | Approved | Serial NO. and Model NO. can be preserved permanently. Serial NO (bzSerialNO) is string type with max length of 15 bytes Model NO (bzModelNO) is string type with max length of 15 bytes
GF.009 | Must | Completed | BIOS (bzBIOSVersion) and application (bzAppVersion) version can be read from MODBUS. Max length of version string is 8 The format of application version is YYMM.xxx where YY is two-digit year, 20 for 2020 for example MM is the acronym of the month that it is released. (JN,FB,MR,AP,MY,JN,JL,AG,SP,OT,NV,DC) and xxx is ordinal number for the release times in the specific month
GF.010 | Optional | Planning | US customary and metric are supported for MODBUS variables.
GF.011 | Must | Completed | Warning code (bzWarningBase) must start from me (excluded). --------------👉 | 9960
GF.012 | Must | Completed | Warning code must be unique.
GF.013 | Must | Completed | Alarm code (bzAlarmBase) must start from me (excluded). --------------------👉 | 10160
GF.014 | Must | Completed | Alarm code must be unique.
GF.015 | Must | Completed | M172 Holding Register Address Range, 8960 - 9959 status (1000) 9960 - 10159 warning (200) 10160 - 10359 alarm (200) 10360 - 10959 configuration (600) 10960 - 13959 'BZ172Lab' reserved 16384 - 18431 nonvolatile configuration (2048) 18431 - 20479 'BZ172Lab' reserved The register address is from 1 (PLC address).
GF.016 | Must | Completed | The 'holding register type' is one and only for data exchange by MODBUS on M172.
GF.017 | Must | In Progress | RS485-2 (CN1) is working as a MODBUS master to manage the I/O boards. 19200 8-E-1 is the parameters for communication. __________________________ I/O board Address ------------------------------------ CSCB1 1 EVD 2 Fan Tacho 3 *CPY 4 __________________________ * CPY is not included in wave 1.
GF.018 | Must | Completed | RS485-1 (CN19) is the customer interface of data exchange by working as a MODBUS slave. By default, the communication parameters are 19200 8-E-1 and the address is 7.
GF.019 | Nice to have | Completed | The GREEN led (the bottom one) indicates the status of the controller. Blinking : Application is working. *The one which is solid on indicates the controller is powered on.
GF.020 | Nice to have | Completed | When there's any warning occurred, the YELLOW led should be blinking to make a visual indication.
GF.021 | Nice to have | Completed | When there's any alarm occurred, the RED led should be blinking as a prompt.
AM |  |  | Ambient Monitoring
AM.001 | Must | Completed | The average return air temperature is calculated by the upper and lower temperature probes. RATu : Upper probe measurement RATl : Lower probe measurement RATg : Average measurement
AM.002 | Must | Completed | The average supply air temperature is calculated by the upper and lower temperature probes. SATu : Upper probe measurement SATl : Lower probe measurement SATg : Average measurement
AM.003 | Must | Completed | The max rack inlet air temperature is calculated by the probes connected to each unit. At least one probe should be available in normal circumstance. RCT1 : Upper probe measurement RCT2 : Lower probe measurement RCTh : Maximum measurement
AM.004 | Must | Approved | One humidity sensor is equipped on the return air side for RH measurement and the dew point can be calculated accordingly. RTH : Return side measurement
AM.005 | Optional | Planning | Humidity sensor presence is configurable. RTH_is_present_cfg is YES or NO, YES by default
AM.006 | Optional | Planning | Outdoor unit (CSCB1) should be able to report the outside amibent temperature. OAT : Outdoor ambient temperature
AM.007 | Must | Completed | Alarm sequence number in this section is from 1
AM.008 | Must | Completed | Alarm[1] : Upper return air temperature sensor fault Conditions : Entry : Upper return temperature readings is not available from M172. Exit : Reading is available. | 10161
AM.009 | Must | Completed | Alarm[2] : Lower return air temperature sensor fault Conditions : Entry : Lower return temperature readings is not available from M172. Exit : Reading is available. | 10162
AM.010 | Must | Completed | Alarm[3] : Upper supply air temperature sensor fault Conditions : Entry : Upper supply temperature readings is not available from M172. Exit : Reading is available. | 10163
AM.011 | Must | Completed | Alarm[4] : Lower supply air temperature sensor fault Conditions : Entry : Lower supply temperature readings is not available from M172. Exit : Reading is available. | 10164
AM.012 | Must | Approved | Alarm[5] : Return air humidity sensor fault Conditions: Entry : RTH_is_present_cfg is YES and RTH is invalid. Exit : Reading is available or RTH_is_present is NO. | 10165
AM.013 | Must | Completed | Warning sequence number in this section is from 1
AM.014 | Must | Completed | Warning[1]: High return air temperature Conditions: Entry : RATg is greater than bzHighReturnTemperatureThresholdCfg for bzHighReturnTemperatureThresholdCfg of period. Exit : RATg is below RATg_max_threshold bzHighReturnTemperatureThresholdCfg is [35, 55]C with default 45C bzHighReturnTemperatureThresholdCfg is [3, 60] minute with default 10 min | 9961
AM.015 | Must | Completed | Warning[2]: High supply air temperature Conditions: Entry : SATg is greater than bzHighSupplyTemperatureThresholdCfg for bzHighSupplyTemperatureThresholdCfg time of period and the actual output of compressor is greater than 95% of the max speed (Hz). Exit : SATg is lower than SATg_max_threshold or the compressor is stopped. bzHighSupplyTemperatureThresholdCfg is [25, 45]C with default 30C bzHighSupplyTemperatureThresholdCfg is [3, 60] minute with default 10 min | 9962
AM.016 | Must | Completed | Warning[3]: None of rack inlet temperature Conditions: Entry : RCTh is not available. Exit : RCTh is available. | 9963
AM.017 | Must | Completed | Warning[4]: High rackinlet air temperature Conditions: Entry : RCTh is greater than bzHighRackinletTemperatureThresholdCfg for bzHighRackinletTemperatureTimeoutCfg time of period. Exit : RCTh is below RCTh_max_threshold bzHighRackinletTemperatureThresholdCfg is [25, 55]C with default 35C bzHighRackinletTemperatureTimeoutCfg is [3, 60] minute with default 10 min | 9964
AM.018 | Must | Approved | Warning[5]: Low humidity Conditions: Entry : RTH_is_present_cfg is YES and RTH is lower than RTH_low_cfg for RTH_timeout_cfg time of period. Exit : RTH is greater than RTH_low_cfg or RTH_is_present_cfg is NO. RTH_low_cfg is (10, 50)% with default 30% RTH_timeout_cfg is [3, 60] minute with default 10 min | 9965
AM.019 | Must | Approved | Warning[6]: High humidity Conditions: Entry : RTH_is_present_cfg is YES and RTH is greater than RTH_high_cfg for RTH_timeout_cfg time of period. Exit : RTH is greater than RTH_high_cfg or RTH_is_present_cfg is NO. RTH_low_cfg is (50, 70)% with default 60% RTH_timeout_cfg is [3, 60] minute with default 10 min | 9966
VF |  |  | Evaporator Fan Control
VF.001 | Must | In Progress | Fan control signal is from 0 to 10vdc and the actual range can be configured. The minimal control signal (EvapFanCtrlSigMin) is configurable and its range is [0, 10)vdc with 2v by default. The maximum control signal (EvapFanCtrlSigMax) is configurable and its range is (2, 10]vdc with 10v by default. EvapFanCtrlSigMax must be greater than EvapFanCtrlSigMin.
VF.002 | Must | In Progress | Fan control command (EvapFanCmd) is always presented by a range of 0 to 100%. The range should match the actual range of control signal, for example, 2 to 9 vdc for 0 to 100 percent.
VF.003 | Must | Pending Approval | A fast DI input (pulse) module from Carel is applied for fan tacho feedback detection. M172 polls the registers by RS485 with standard modbus protocol to get the meausrement of each fan.
VF.004 | Must | Approved | Each fan can have a tacho feedback by RPM and the estimated speed can be calculated based on EvapFanCmd. EvapFanTachoAct_0...5 EvapFanTachoEst_0…5
VF.005 | Optional | Approved | Airflow (EvapAirflow) can be calculated by total RPM from the fans having tacho feedback.
VF.006 | Optional | Approved | Fan tacho feedback can be enabled or disabled.
VF.007 | Must | Completed | The working mode of evaporator fan is selected by the configurable fan strategy (bzEvaporatorFanStrategyCfg). There are three types of strategies, InRow_CACS(0), HACS_RACS(1) and CONSTANT_SPD(2). By default, it should be '0'.
VF.008 | Must | Completed | The configurable cool setpoint (bzCoolSetpointCfg) is from 15 to 30 celcius degree and the default is 18C.
VF.009 | Must | Completed | The configurable delta-T setpoint (bzDeltaTSetpointCfg) is from 2 to 20 celcius degree and the default is 10C.
VF.010 | Must | Completed | With auto mode, fan output is regulated by a PID controller or a constant speed which depends on the unit status, mode and fan control strategies. ______________________________________________________________________ STATUS MODE FAN STRATEGY FAN COMMAND (EvapFanStrategy_cfg) (EvapFanCmd) -------------------------------------------------------------------------------------------------- OFF any any full stop (0%) -------------------------------------------------------------------------------------------------- ON COOL InRow_CACS PID(CoolSP_cfg, RCTh) -------------------------------------------------------------------------------------------------- ON COOL HACS_RACS PID(SATSP_cfg + DeltaSP_cfg, RATg) -------------------------------------------------------------------------------------------------- ON COOL FIX a configurable constant speed -------------------------------------------------------------------------------------------------- MAINTENANCE any FIX a constant speed ______________________________________________________________________ Refer to 'Evaporator Fan Control SM' in 'Diagrams' sheet.
VF.011 | Must | Completed | PID output range is limited with the configurable min(bzMinimumEvaporatorFanSpeedCfg) and max(bzMaximumEvaporatorFanSpeedCfg) fan speed when the unit is in normal operation. bzMinimumEvaporatorFanSpeedCfg is from 0% to 50% with default 30% bzMaximumEvaporatorFanSpeedCfg is from 60% to 100% with default 100%
VF.012 | Optional | On Hold | When the unit is 'ON' and the compressor is not running, fan should be running with a constant speed (20%).
VF.013 | Must | Completed | If the inputs from the temperature sensors are not available and fan strategy is InRow_CACS, fan speed should be set to bzMaximumEvaporatorFanSpeedCfg.
VF.014 | Must | Completed | If the inputs from the temperature sensors are not available and fan strategy is HACS_RACS, fan speed should be set to bzMinimumEvaporatorFanSpeedCfg.
VF.015 | Must | Completed | If pan full fault alarm (8090) occurred, the evaporator fan should be stopped immediately to shun the possiblity of blowing the condensate out.
VF.016 | Must | Approved | When the fan is running (command and tacho are greater than 0), the working hours should be traced with a resolution of 1 hour. EvapFanRunHours_0…5
VF.017 | Must | Approved | Fan run hours threshold (EvapFanRunHoursThreshold_cfg) is from 8736 (1 year) to 65535. 20208 (3 years) is default.
VF.018 | Must | Approved | Warning sequence number in this section is from 20
VF.019 | Must | Approved | Warning[20]: Evaporator Fan 1 Check Conditions: Entry : EvapFanTachoAct_0 cannot match EvapFanTachoEst_0+/-800rpm and EvapFanCmd >= EvapFanCmdMin_cfg. Exit : EvapFanTachoAct_0 cannot match EvapFanTachoEst_0+/-800rpm or EvapFanTachoAct_0 is 0%. | 9980
VF.020 | Must | Approved | Warning[21]: Evaporator Fan 2 Check Conditions: Entry : EvapFanTachoAct_1 cannot match EvapFanTachoEst_1+/-800rpm and EvapFanCmd >= EvapFanCmdMin_cfg. Exit : EvapFanTachoAct_1 cannot match EvapFanTachoEst_1+/-800rpm or EvapFanTachoAct_1 is 0%. | 9981
VF.021 | Must | Approved | Warning[22]: Evaporator Fan 3 Check Conditions: Entry : EvapFanTachoAct_2 cannot match EvapFanTachoEst_2+/-800rpm and EvapFanCmd >= EvapFanCmdMin_cfg. Exit : EvapFanTachoAct_2 cannot match EvapFanTachoEst_2+/-800rpm or EvapFanTachoAct_2 is 0%. | 9982
VF.022 | Must | Approved | Warning[23]: Evaporator Fan 4 Check Conditions: Entry : EvapFanTachoAct_3 cannot match EvapFanTachoEst_3+/-800rpm and EvapFanCmd >= EvapFanCmdMin_cfg. Exit : EvapFanTachoAct_3 cannot match EvapFanTachoEst_3+/-800rpm or EvapFanTachoAct_3 is 0%. | 9983
VF.023 | Must | Approved | Warning[24]: Evaporator Fan 5 Check Conditions: Entry : EvapFanTachoAct_4 cannot match EvapFanTachoEst_4+/-800rpm and EvapFanCmd >= EvapFanCmdMin_cfg. Exit : EvapFanTachoAct_4 cannot match EvapFanTachoEst_4+/-800rpm or EvapFanTachoAct_4 is 0%. | 9984
VF.024 | Must | Approved | Warning[25]: Evaporator Fan 6 Check Conditions: Entry : EvapFanTachoAct_5 cannot match EvapFanTachoEst_5+/-800rpm and EvapFanCmd >= EvapFanCmdMin_cfg. Exit : EvapFanTachoAct_5 cannot match EvapFanTachoEst_5+/-800rpm or EvapFanTachoAct_5 is 0%. | 9985
VF.025 | Optional | Approved | Fan fault warning is configurable.
VF.026 | Must | Approved | Warning[26]: Evaporator Fan 1 Lifecycle Conditions: Entry : EvapFanRunHours_0 > EvapFanRunHoursThreshold_cfg. Exit : EvapFanRunHours_0 < EvapFanRunHoursThreshold_cfg. | 9986
VF.027 | Must | Approved | Warning[27]: Evaporator Fan 2 Lifecycle Conditions: Entry : EvapFanRunHours_1 > EvapFanRunHoursThreshold_cfg. Exit : EvapFanRunHours_1 < EvapFanRunHoursThreshold_cfg. | 9987
VF.028 | Must | Approved | Warning[28]: Evaporator Fan 3 Lifecycle Conditions: Entry : EvapFanRunHours_2 > EvapFanRunHoursThreshold_cfg. Exit : EvapFanRunHours_2 < EvapFanRunHoursThreshold_cfg. | 9988
VF.029 | Must | Approved | Warning[29]: Evaporator Fan 4 Lifecycle Conditions: Entry : EvapFanRunHours_3 > EvapFanRunHoursThreshold_cfg. Exit : EvapFanRunHours_3 < EvapFanRunHoursThreshold_cfg. | 9989
VF.030 | Must | Approved | Warning[30]: Evaporator Fan 5 Lifecycle Conditions: Entry : EvapFanRunHours_4 > EvapFanRunHoursThreshold_cfg. Exit : EvapFanRunHours_4 < EvapFanRunHoursThreshold_cfg. | 9990
VF.031 | Must | Approved | Warning[31]: Evaporator Fan 6 Lifecycle Conditions: Entry : EvapFanRunHours_5 > EvapFanRunHoursThreshold_cfg. Exit : EvapFanRunHours_5 < EvapFanRunHoursThreshold_cfg. | 9991
VF.032 | Must | Approved | Warning[32]: Fan Tacho Module Offline Conditions: Entry : Registers cannot be polled from Carel DI module from M172. Exit : Polling success. | 9992
CW |  |  | Chilled Water Valve Control
CW.001 | - | - | TBD
EC |  |  | EEV Control
EC.001 | Must | Pending Approval | EEV is driven by an EVD controller through modbus communication on RS485. Modbus registers for operation??
EC.002 | Must | Completed | The evaporator coil superheat (Tevap_sh) is calculated by EOT and EOP.
EC.003 | Must | Completed | A temperature probe (EOT) installed on the outlet side of the coil is for the suction temperature measurement (Tcoil).
EC.004 | Must | In Progress | A pressure probe (EOP) installed on the outlet side of the coil is for the suction pressure measurement (Pcoil).
EC.005 | Must | In Progress | ______________________________________________________________________ UNIT STATUS COMMAND -------------------------------------------------------------------------------------------------- OFF Configurable pre-position (EEV_preopen_cfg) -------------------------------------------------------------------------------------------------- ON PID(EvapSH_SP, Tevap_sh) -------------------------------------------------------------------------------------------------- ON Gradually close when compressor pump down is executed -------------------------------------------------------------------------------------------------- MAINTENANCE depends on user's instruction ______________________________________________________________________ Refer to 'EEV Control SM' in 'Diagrams' sheet.
EC.006 | Must | Completed | The EEV minimal opening (bzMinimumEEVOpeningCfg) for auto control is configurable. bzMinimumEEVOpeningCfg is from 0% to 50% with default 20%.
EC.007 | Must | Completed | The EEV pre-position (bzEEVPreOpeningCfg) is configurable. bzEEVPreOpeningCfg is from [0, 100] % with default 40%
EC.008 | Must | Completed | The target evaporator superheat (bzEvapSuperheatSetpointCfg) is configurable. bzEvapSuperheatSetpointCfg is from [1, 30] Celcius degree with default 8c.
EC.009 | Must | Completed | A deadband(bzEvapSuperheatDeadbandCfg) is set for EEV auto control to make the performance of PID output more stable. bzEvapSuperheatDeadbandCfg is from [0, 3] with default 1 celcius degree that gives ±1c tolerance to the set point.
EC.010 | Must | Completed | EEV working time (EEVRunHours) should be traced with a percision of an hour.
EC.011 | Must | Completed | Warning sequence number in this section is from 50
EC.012 | Must | Approved | Warning[50] : Low Evaporator Superheat Entry : EEV is at minimal position and Tevap_sh is lower than EvapLowSH_threshold_cfg for EvapLowSH_timeout_cfg. Exit : Tevap_sh is greater than EvapLowSH_threshold_cfg. EvapLowSH_threshold_cfg is from [1, 30] Celcius degree. 10C is default. EvapLowSH_timeout_cfg is from [10, 600] seconds. 180s is default. | 10010
EC.013 | Must | Approved | Low Evaptorator Superheat' should be ignored for a few moment (EvapLowSH_forgiven_timeout_cfg) each time once the compressor is truly started. EvapLowSH_forgiven_timeout_cfg is from [10, 600] seconds. 180s is default.
EC.014 | Must | Completed | Warning[51] : EEV Lifecycle Entry : bzEEVRunHourLog > bzEEVRunHourThresholdCfg. Exit : bzEEVRunHourLog < bzEEVRunHourThresholdCfg. bzEEVRunHourThresholdCfg is from [8736, 65535] with default 20208 | 10011
EC.015 | Must | Pending Approval | Warning[52] : EVD check Entry : Any warning reported by EVD module is captured. Exit : No warning from EVD module. | 10012
EC.016 | Must | Approved | Alarm sequence number in this section is from 50
EC.017 | Must | Completed | Alarm[50] : Coil temperature sensor fault Conditions : Entry : Tcoil is not available from M172. Exit : Reading is available. | 10210
EC.018 | Must | Approved | Alarm[51] : Coil pressure sensor fault Conditions : Entry : Pcoil is not available from M172. Exit : Reading is available. | 10211
EC.019 | Must | Approved | Alarm[52] : EVD offline Conditions : Entry : M172 cannot poll registers from EVD driver. Exit : Polling registers success. | 10212
EC.020 | Must | Approved | Alarm[53] : Persistent Low Superheat Entry : 'Low Evaporator Superheat' occurred EvapLowSH_max_times_cfg within an hour. Exit : Manually reset EvapLowSH_max_times_cfg is from [1, 60] with default 3. | 10213
EC.021 | Must | Pending Approval | Alarm[54] : EVD Internal Fault Entry : Any alarm reported by EVD module is captured. Exit : No alarm from EVD module. | 10214
SV |  |  | Soleniod Valve Control
SV.001 | Must | Completed | The soleniod valve (liquid pipe valve) is controlled by a digital ouput (LSV).
SV.002 | Must | In Progress | ______________________________________________________________________ UNIT STATUS COMMAND -------------------------------------------------------------------------------------------------- OFF OFF -------------------------------------------------------------------------------------------------- ON ON: when the compressor is requested to start up -------------------------------------------------------------------------------------------------- ON OFF: after the compressor is fully stopped -------------------------------------------------------------------------------------------------- MAINTENANCE depends on user's instruction ______________________________________________________________________ Refer to 'Soleniod Valve Control SM' in 'Diagrams' sheet.
SV.003 | Must | Completed | Run hour (bzSoleniodValveRunhourLog) should be traced with a percision of an hour.
SV.004 | Must | Completed | Warning sequence number in this section is from 60
SV.005 | Must | Completed | Warning[60] : LSV Lifecycle Entry : bzSoleniodValveRunhourLog > bzSolenoidValveRunhourThresholdCfg. Exit : bzSoleniodValveRunhourLog < bzSolenoidValveRunhourThresholdCfg. bzSolenoidValveRunhourThresholdCfg is from [8736, 65535] with default 20208 | 10020
CC |  |  | Compressor Control
CC.001 | Must | Pending Approval | Compressor driven by VFD is controlled by the outdoor control board (CSCB1) and the indoor controller (M172) will act as a Modbus master to communicate with CSCB1 by RS485 bus.
CC.002 | Must | Pending Approval | Compressor general management will be handled by CSCB1. - Driven by VFD - Perform capacity control requested by the indoor controller - Envelope control - High pressure protection - Low pressure protection - Oil return management Refer to 'SANHUA CSCB1 Manual' wich I don't have so far:)
CC.003 | Must | Approved | Compressor and VFD status should be polled periodically.
CC.004 | Must | In Progress | ______________________________________________________________________ UNIT STATUS COMMAND -------------------------------------------------------------------------------------------------- OFF Off -------------------------------------------------------------------------------------------------- ON PID(SAT_SP, SATg) -------------------------------------------------------------------------------------------------- SERVICE depends on user's instruction ______________________________________________________________________ Refer to 'Compressor Control SM' in 'Diagrams' sheet.
CC.005 | Must | Completed | Whe RATg is greater than 20C and SATg is greater than SAT_SP, the compressor will be turned on and regulated by a PID controller. If RATg is not available, ignore it.
CC.006 | Must | Completed | Maintain the minimal compressor speed (bzMinimumCompressorCommandCfg) when PID output is set to minimum. bzMinimumCompressorCommandCfg is from [0, 100] % with default 20%.
CC.007 | Must | Completed | When the suction pressure is lower than a threshold (bzCompressorPumpDownThresholdCfg) or timeout (bzCompressorPumpDownTimeout) is expired, pumpdown process is end. bzCompressorPumpDownThresholdCfg is from [1.0, 10.0] bar with default 7.38bar bzCompressorPumpDownTimeoutCfg is from [5, 60] second with default 30s.
CC.008 | Must | Completed | When the compressor is executing pump down process, a configurable constant speed (bzCompressorPumpDownCommandCfg) is given. bzCompressorPumpDownCommandCfg is from [bzMinimumCompressorCommandCfg, 100] % with default 78%
CC.009 | Must | Completed | When SATg is lower than a minimal temperature threshold (bzMinimalSupplyAirTemperatureCfg) and the integral of the differential to the setpoint is greater than 480C*S, the compressor will be turned off. bzMinimalSupplyAirTemperatureCfg is from [5, 15] c with default 12.5c
CC.010 | Must | Completed | The configurable supply air temperature setopint (bzSupplyAirSetpoint) is one of the inputs for compressor speed regulation (cooling capacity control). bzSupplyAirSetpoint is from [15, 30] Celcius degree with default 18c.
CC.011 | Must | Approved | The compressor should start and raise the max speed gradually if SATg is not available when the compressor is off. When SATg is recovered, the compressor control is back to normal process.
CC.012 | Must | Approved | The compressor will keep the current speed if SATg is not available when it is in normal control.
CC.013 | Must | Approved | If any of the EEV fault (alarm) is detected, the compressor should be shutdown immediately.
CC.014 | Must | Pending Approval | If any of critical alarms from CSCB that can damanage the compressor are detected, the compressor should be shutdown immediately.
CC.015 | Must | Approved | If leakage detection alarm (8100) occurred, the compressor should be shutdown immediately.
CC.016 | Must | Approved | If pan full fault alarm (8090) occurred, the compressor should be shutdown immediately.
CC.017 | Must | Approved | Alarm sequence number in this section is from 70
CC.018 | Must | Approved | Alarm[70] : CSCB1 Offline Entry : M172 cannot poll the registers from CSCB1 Exit : Communication is good | 10230
CC.019 | Must | Pending Approval | Any alarms from CSCB1 about the compressor and vfd should be also mapped to the modbus registers.
CC.020 | Must | Completed | Warning sequence number in this section is from 70
CC.021 | Must | Completed | Warning[70] : Compressor Lifecycle Entry : bzCompressorRunHourLog > bzCompressorRunHourThresholdCfg. Exit : bzCompressorRunHourLog < bzCompressorRunHourThresholdCfg. bzCompressorRunHourThresholdCfg is from [8736, 65535] with default 20208 | 10030
CF |  |  | Condensor Fan Control
CF.001 | Must | Pending Approval | Condensor fan is driven by the outdoor control board (CSCB1) or speed regulator?
CF.002 | Must | Pending Approval | Fan status should be polled periodically?
CP |  |  | Condensate Pump Control
CP.001 | Must | Completed | The firmware should be able to detect the condensate level in the pan by two water flow switches, a lower one (CPSl) and a upper (CPSu).
CP.002 | Must | Completed | ______________________________________________________________________ UNIT STATUS PUMP COMMAND -------------------------------------------------------------------------------------------------- ON or OFF ON: when the lower switch is detected -------------------------------------------------------------------------------------------------- ON or OFF OFF: when the lower switch is back to normal and bzCondensatePumpDelay2OffCfg is expired -------------------------------------------------------------------------------------------------- MAINTENANCE depends on user's instruction ______________________________________________________________________ Refer to 'Condensate Pump Control SM' in 'Diagrams' sheet.
CP.003 | Must | Completed | Pump running timeout (bzCondensatePumpDelay2OffCfg) is configurable. bzCondensatePumpDelay2OffCfg is from [10, 600] seconds with default 30s.
CP.004 | Must | Completed | Alarm sequence number in this section is from 90
CP.005 | Must | Completed | Alarm[90] : Pan Full Fault Entry : CPSl is detected (switch is closed). Exit : switch is opened. | 10250
CP.006 | Must | Completed | Warning sequence number in this section is from 90
CP.007 | Must | Completed | Warning[90] : Condensate Pump Lifecycle Entry : bzCondensatePumpRunhourLog is greater than bzCondensatePumpRunhourThresholdCfg. Exit : bzCondensatePumpRunhourLog is less than bzCondensatePumpRunhourThresholdCfg. bzCondensatePumpRunhourThresholdCfg is from [8736, 65535] with default 20208 | 10050
BO |  |  | General Binary Outputs Control
BO.001 | Must | Completed | When the unit status is 'ON', a digital output (UOS) is energized to indicate the unit is in auto operation. Refer to 'M172 IO Map'
BO.002 | Must | Completed | The actual output of UOS can is configurable(bzUnitStatusRelayCfg), by default the closed status of it means the unit is 'ON'.
BO.003 | Must | In Progress | When there's any alarm reported by the firmware, a digital output (ALS) is energized to indicate major fault is detected on the unit. Refer to 'M172 IO Map'
BO.004 | Must | Completed | The actual output of ALS is configurable (bzMajorAlarmRelayCfg), by default the closed status of it means there's alarm.
UO |  |  | Unit Operation
UO.001 | Must | Completed | The unit is operational with four status, ON, STARTUP_DELAY, OFF and MAINTENANCE. When the status is OFF, all the actuators are fully stopped (except condensate pump). When the status is ON, the outputs of the actuators will follow its own protocol. When the status is MAINTENANCE, the outputs of the actuators will follow its own protocol. STARTUP_DELAY is a dummy status that is only for a delay to avoid electric impact to the grid when multiple units are requested to start up at the same time. Refer to 'Unit Status SM' in Diagrams sheet.
UO.002 | Must | Completed | Unit status can be set anytime through unit command (bzUnitModeCfg). bzUnitModeCfg is ON, OFF or MAINTENANCE (refer to Modbus Register Map)
UO.003 | Must | Completed | MAINTENANCE mode command should not be stored permanently.
UO.004 | Must | Completed | A binary hardware input (RSS) can override 'ON' status of the unit by putting it into 'OFF'.
UO.005 | Must | Completed | When the status is set to 'MAINTENANCE', a configurable timeout (bzUnitMainteanceTimeoutCfg) will be set. bzUnitMainteanceTimeoutCfg is from [5, 10080] minutes with default 10.
UO.006 | Must | Completed | When the maintenance mode exits, all actuators should be stopped. And when the mode is activated again, all the actuators should be stopped until the manual command is given.
UO.007 | Must | Completed | Unit 'MODE' (bzUnitStatus) is read only on Modbus. (rfer to Modbus Register Map)
UO.008 | Must | Completed | Statup delay (bzUnitStartupDelayCfg) is configurable. bzUnitStartupDelayCfg is from [0, 300] seconds with default 0.
UO.009 | Must | Completed | Warning sequence number in this section is from 100
UO.010 | Must | Completed | Warning[100] : Autopilot Disengaged Entry : Unit status is MAINTENANCE. Exit : Unit status is NOT maintenance. | 10060
UO.011 | Must | Completed | Warning[101] : Unit Lifecycle Entry : bzUnitRunhourLog is greater than bzUnitRunhourThresholdCfg. Exit : bzUnitRunhourLog is less than bzUnitRunhourThresholdCfg. bzUnitRunhourThresholdCfg is from [8736, 65535] with default 20208 | 10061
UO.012 | Must | Completed | Alarm sequence number in this section is from 100
UO.013 | Must | Completed | Alarm[100] : Remote Shutdown Entry : RSS is detected (switch is closed). Exit : switch is opened. | 10260
UO.014 | Must | Completed | Alarm[101] : Airfilter Clogged Detection Entry : ACD is detected (switch is closed). Exit : switch is opened. | 10261
UO.015 | Must | Completed | Alarm[102] : Leakage Detection Entry : LKD is detected (switch is closed). Exit : switch is opened. | 10262
UO.016 | Must | Completed | Alarm[103] : Airfilter Lifecycle Entry : bzAirfilterRunhourLog is greater than bzAirfilterRunhourThresholdCfg. Exit : bzAirfilterRunhourLog is less than bzAirfilterRunhourThresholdCfg. bzAirfilterRunhourThresholdCfg is from [8736, 65535] with default 20208 | 10263
GP |  |  | Group Operation
GP.001
Insert new row before this

## Tasks
ID | Task | Due | Days | PRI | BL | PROG | Owners | Prerequisites | Deliverables
DM | Documentary and Meetings | 2021-06-01 | 72 |  |  | 30%
DW.001 | Draft version of FRS (combined with HLD) | 2021-01-25 | 0 | M | 1 | 100%
DW.002 | Get outdoor unit operation spec from SANHUA | 2021-03-01 | 6 | H | 1 | 0% |  | SANHUA inputs
DW.003 | Review and update FRS and HLD | 2021-03-01 | 6 | M |  | 40%
DW.004 | Get a sample of 'flying master' implementation from Eliwell team for the evaluation of group control on tech. | 2021-04-01 | 29 | L |  | 0% |  | Get support from Eliwell
DW.005 | MODBUS register map for all users | 2021-06-01 | 72 | L |  | 0%
DW.006 | Get EVD driver module spec | 2021-03-01 | 6 | M |  | 0% |  | Eliwell EVD manual
DW.007 | Get Carel fast DI module spec | 2021-02-11 | 0 | L |  | 100% |  | Carel fast DI module manual
DW.008 | Get contact window for M172 tech support from IT team | 2021-03-01 | 6 | H |  | 0% |  | WHO ARE U?!
0
0
0
TS | Test Bench Setup | 2021-04-01 | 29 |  |  | 51.67%
TS.001 | Collect hardware stuff | 2021-03-01 | 6 | H |  | 66.67% |  | Hardware stuff ready | [✔] M172 controllers x 2 [🕒] CSCB x 1 [🕒] EVD module x 1 [✔] Carel DI module x 1 [✔] 24vdc power supply x 1 [✔] 24vac power supply x 1 [✔] temperature sensor x 8 'Carel' Jan.26th [🕒] humidity sensor x 1 [🕒] pressure sensor x 1 [✔] 4-20mA source (pressure sensor) x 1 [❌] < 2k Hz signal source x 8 [🕒] EEV valve x 1 [✔] 24v LED (DO indicator) x 8 [✔] voltage meter (AO) x 2 'Carel' Jan.26th [✔] switch (DI simulator) x 8 'Carel' Jan.26th [✔] wires
TS.002 | Test bench build | 2021-03-10 | 13 | H |  | 40% |  |  | Refer to saaral.testbench.jpg
TS.003 | MODBUS communication on RS485 monitor | 2021-04-01 | 29 |  |  | 100% |  |  | IrACdx36.mb.monitor.com28.192008e1.exe
TS.004 | Test supervisor tool development | 2021-04-01 | 29 | L | 1 | 0% |  |  | [] IrACdx36.exe?
0
0
MI | M172 Implementation | 2021-06-01 | 72 |  |  | 49.22%
MI.001 | Project preparation and high level design | 2021-02-01 | 0 |  |  | 100% |  |  | [✔] Code repository setup (Github) [✔] Project creation
MI.002 | Program framework | 2021-03-01 | 6 |  |  | 100% |  |  | [✔] Real mode [✔] Object model [✔] Hardware interfaces [✔] Timer [✔] Slave device [✔] MODBUS communication model [✔] NVM [✔] Warning and alarm [✔] Actuator working time [✔] Task model
MI.003 | DDF overall design | 2021-03-01 | 6 | M |  | 100% |  |  | [✔] Modbus holding register address section [✔] BZ172Lab.py for doc generation
MI.004 | Humidity and pressure sensor | 2021-03-01 | 6 | H |  | 0% |  |  | [] Humidity sensor reading [] Pressure sensor reading [] Dew point caluclation [] Saturation temperature calculation
MI.005 | EVD and valve | 2021-03-07 | 10 | H |  | 0% |  |  | [] EVD communication [] EEV drive
MI.006 | CSCB1 | 2021-03-15 | 16 | H |  | 0% |  |  | [] CSCB1 communication [] Compressor drive
MI.007 | Pulse measurement (Carel h-DI module) test | 2021-02-10 | 0 |  |  | 100% |  |  | [✔] Modbus communication [✔] Measurement readings check 1kHz from M172 AO4 gives 992 around readings and 500Hz creates reading of 495-497
MI.008 | Component design | 2021-03-20 | 20 |  |  | 55% |  |  | [✔] Temperature sensor [] Humidity sensor [] Fan tacho [✔] Solenoid valve [✔] Relays [✔] Switches [✔] Evaporator Fan [🕒] EVD and EEV [🕒] Compressor and VFD
MI.009 | Unit 'MAINTENANCE' mode | 2021-03-25 | 24 |  |  | 40% |  |  | [✔] Evaporator Fan [✔] Pump [✔] Solenoid valve [🕒] EEV [🕒] Compressor (VFD)
MI.010 | Unit control | 2021-03-01 | 6 |  |  | 100% |  |  | FRS.UO FRS.BO
MI.011 | Ambinent temperature management | 2021-03-01 | 6 |  |  | 80% |  |  | FRS.AM
MI.012 | Condensate pump control | 2021-03-01 | 6 |  |  | 100% |  |  | FRS.CP
MI.013 | Evaporator fan control | 2021-04-15 | 39 |  |  | 50% |  |  | FRS.VF
MI.014 | EEV control | 2021-04-20 | 42 |  |  | 30% |  |  | FRS.EC
MI.015 | Outdoor unit control | 2021-04-30 | 50 |  |  | 1% |  |  | FRS.CC FRS.CF
MI.017 | Warnings and alarms | 2021-05-13 | 59 |  |  | 30% |  |  | FRS.xx
MI.018 | First release | 2021-05-15 | 60 |  | 1 | 0%
0
| Final release | 2021-07-01 | 94 |  | 1 | 0%
0
0
DV | Development Verification | 2021-07-01 | 94 |  |  | 10.83%
DV.001 | Temperature sensor | 2021-04-01 | 29 |  |  | 50% |  |  | [✔] Reading [] Range [] Accuracy
DV.002 | Humidity sensor | 2021-04-01 | 29 |  |  | 0% |  |  | [] Reading [] Range [] Accuracy
DV.003 | Tacho meter | 2021-04-01 | 29 |  |  | 0% |  |  | [] Reading [] Range [] Accuracy
DV.004 | Pressure sensor | 2021-04-01 | 29 | H |  | 0% |  |  | [] Reading [] Range [] Accuracy
DV.005 | Communication to CAREL DI board | 2021-04-01 | 29 |  |  | 80% |  |  | [✔] Communication [✔] Register polling traverse [🕒] Persistent communication [🕒] Communication fault and recovery
DV.006 | Communication to DI board | 2021-04-01 | 29 |  |  | 0% |  |  | [] Communication [] Register polling traverse [] Persistent communication [] Communication fault and recovery
DV.007 | Communication to CSCB1 | 2021-04-01 | 29 | H |  | 0% |  |  | [] Communication [] Register polling traverse [] Persistent communication [] Communication fault and recovery
DV.008 | Communication from supervisor (HMI) | 2021-04-01 | 29 |  |  | 0% |  |  | [] Communication [] Persistent communication [] Communication fault and recovery
DV.009 | Evaporator fan | 2021-04-01 | 29 |  |  | 0% |  |  | [] Operation [] Tacho reading
DV.010 | Solenoid valve | 2021-04-01 | 29 |  |  | 0% |  |  | [] Operation
DV.011 | EEV | 2021-04-01 | 29 | H |  | 0% |  |  | [] Operation
DV.012 | VFD (compressor) | 2021-04-01 | 29 | H |  | 0% |  |  | [] Operation
0
0
0
0
0
0
|  |  | 0 |  |  | #DIV/0!
0
0
0
0
|  |  | 0 |  |  | #DIV/0!
0
0
0
0
0
|  |  | 0 |  |  | #DIV/0!
0
0
0
0
0
|  |  | 0 |  |  | #DIV/0!
0
0
0
0
0
Insert new rows above this one
Formulas:
Days = IF(OR(ISBLANK(Table1[[#This Row],[Due]]),TODAY()>Table1[[#This Row],[Due]]),0,NETWORKDAYS(TODAY(),Table1[[#This Row],[Due]]))
Note on E2: BoTong ZHANG: It will be calculated by the time range
Note on G2: BoTong ZHANG: A value greater than 0 means it should be a milestone
Note on H2: BoTong ZHANG: 0: means not started 100: means done any value between min and max is the estimation of work has been done

## M172 IO Map
AI (M172) | Type | Name | Expansion Board (Carel) | Type | Name
AI1 | NTC | Upper Return Air Temperature (RATu) | ? | RS485 | To M172
AI2 | NTC | Lower Return Air Temperature (RATl) | DI1 | Pulse | Evaporator Fan 1 Tacho
AI3 | NTC | Upper Supply Air Temperature (SATu) | DI2 | Pulse | Evaporator Fan 2 Tacho
AI4 | NTC | Lower Supply Air Temperature (SATl) | DI3 | Pulse | Evaporator Fan 3 Tacho
AI5 | NTC | Rack Inlet Air Temperature 1 (RCT1) | DI4 | Pulse | Evaporator Fan 4 Tacho
AI6 | NTC | Rack Inlet Air Temperature 2 (RCT2) | DI5 | Pulse | Evaporator Fan 5 Tacho
AI7 | NTC | Evaporator Coil Outlet Temperature (EOT) | DI6 | Pulse | Evaporator Fan 6 Tacho
AI8 | NTC | reserved
AI9 | 4-20mA | Return Air Humidity (RAH)
AI10 | 4-20mA | Evaporator Coil Outlet Pressure (EOP)
AI11 | 0-10vdc | reserved
AI12 | 0-10vdc | reserved
*Type of input must be in pair
AO (M172) | Type | Name | EVD (M172 Expansion) | Type | Name
AO1 | 0-10vdc | Evaporator Fan Group 1 (EVF1) | ? | RS485 | To M172
AO2 | 0-10vdc | Evaporator Fan Group 1 (EVF2)
AO3 | 0-10vdc | reserved
AO4 | 0-10vdc | reserved
AO5 | 0-10vdc | reserved
AO6 | 0-10vdc | reserved
DI (M172) | Type | Name
DI1 | Pulse | reserved
DI2 | Pulse | reserved
DI3 | Switch | Remote shutdown input (RSS)
DI4 | Switch | Airfilter clogged detection (ACD)
DI5 | Switch | Leak detection (LKD)
DI6 | Switch | Upper condensate pan switch (CPSu)
DI7 | Switch | Lower condensate pan switch (CPSl)
DI8 | Switch | reserved
DI9 | Switch | reserved
DI10 | Switch | reserved
DI11 | Switch | reserved
DI12 | Switch | reserved
DO (M172) | Type | Name
DO1 | Relay | Unit on/off status (UOS)
DO2 | Relay | Alarm status (ALS)
DO3 | Relay | Fan PSU 1 (FPS1)
DO4 | Relay | Fan PSU 2 (FPS2)
DO5 | Relay | Condensate pump (CPD)
DO6 | Relay | Liquid Solenoid Valve (LSV)
DO7 | Relay | reserved
DO8 | Relay | reserved
DO9 | Relay | Heater 1 (HT1)
DO10 | Relay | Heater 2 (HT2)
DO11 | Relay | reserved
DO12 | Relay | reserved
COM(M172) | Type | Name
CN18 | CAN | Group
CN19 | RS485 | Slave to local HMI
CN1 | RS485 | Master to expansion boards and CSCB
CN20 | Ethernet | reserved
CN17 | USB | Program download interface
CN16 | USB | Online debug

## Diagrams
@startuml Unit Status SM
[*] --> OFF
OFF : All actuators are fully stopped.
OFF --> STARTUP_DELAY : evTurnUnitOn
OFF --> MAINTENANCE : evTurnMaintenanceOn
STARTUP_DELAY : No actions.
STARTUP_DELAY --> ON : evStartupDelayTimeout
STARTUP_DELAY --> OFF: evTurnUnitOff
ON : The actuators is regulated\nby control logic.
ON --> OFF : evTurnUnitOff\nOR\nevRemoteShutdown
MAINTENANCE : Outputs of the actuators follow\n the instructions from operators.
MAINTENANCE --> OFF : evMaintenanceTimeout
@enduml
@startuml Condensate Pump Control SM
[*] --> OFF
OFF : Pump is stopped.
OFF --> ON : evLowWaterFlowSwitchOn
ON : Pump is running.
ON --> ON_DELAY : evLowWaterFlowSwitchOff
ON_DELAY : Pump is running for a while
ON_DELAY --> OFF : evPumpOnDelayTimeout
ON_DELAY --> ON : evLowWaterFlowSwitchOn
@enduml
@startuml Solenoid Valve Control SM
[*] --> OFF
OFF : Valve is closed.
OFF --> ON : Compressor status is 'PRESTART' or\n'STARTED'
ON : Valve is opened.
ON --> OFF : Compressor status is 'PUMPDOWN' or\n'STOPPED'
@enduml
@startuml Evaporator Fan Control SM
[*] --> OFF
OFF : Fan is fully stopped.
OFF --> ON : Unit status is 'ON'
state ON {
[*] --> STANDBY_SPEED
STANDBY_SPEED: Minimal speed without compressor running
STANDBY_SPEED --> VARIABLE_SPEED_RACK : evCompressorRunning
STANDBY_SPEED --> VARIABLE_SPEED_RAT : evCompressorRunning
STANDBY_SPEED --> FIX_SPEED : evCompressorRunning
VARIABLE_SPEED_RACK: PID(cool setpoint, Tmax_rack)
VARIABLE_SPEED_RACK --> VARIABLE_SPEED_RAT : evIndoorFanStrategyUpdate
VARIABLE_SPEED_RACK --> FIX_SPEED : evIndoorFanStrategyUpdate
VARIABLE_SPEED_RACK --> EXCEPTION_SPEED : evBadRackAirMax
VARIABLE_SPEED_RACK --> STANDBY_SPEED : evCompressorStopped
VARIABLE_SPEED_RAT: PID(Trat_sp, Trat_avg)
VARIABLE_SPEED_RAT --> VARIABLE_SPEED_RACK : evIndoorFanStrategyUpdate
VARIABLE_SPEED_RAT --> FIX_SPEED : evIndoorFanStrategyUpdate
VARIABLE_SPEED_RAT --> EXCEPTION_SPEED : evBadReturnAirAvg
VARIABLE_SPEED_RAT --> STANDBY_SPEED : evCompressorStopped
FIX_SPEED: Given constant speed
FIX_SPEED --> VARIABLE_SPEED_RACK : evIndoorFanStrategyUpdate
FIX_SPEED --> VARIABLE_SPEED_RAT : evIndoorFanStrategyUpdate
FIX_SPEED --> STANDBY_SPEED : evCompressorStopped
EXCEPTION_SPEED: Min or max speed by strategy
EXCEPTION_SPEED --> VARIABLE_SPEED_RACK : evGoodRackAirMax
EXCEPTION_SPEED --> VARIABLE_SPEED_RAT : evGoodReturnAirAvg
EXCEPTION_SPEED --> STANDBY_SPEED : evCompressorStopped
}
ON --> OFF : Unit status is 'OFF'
@enduml
@startuml EEV Control SM Control SM
[*] --> INIT
INIT : Fully closed the valve and then\nmove to the pre-position
INIT --> OFF : EVD is good
OFF : Set to a configurable idle position.
OFF --> ON : Unit status is 'ON'
OFF --> INIT : EVD fault occurred
state ON {
[*] --> PRE_OPEN
PRE_OPEN : Set to a configurable pre position
PRE_OPEN --> AUTO : Compressor is about to run
AUTO : PID control based on evaproator superheat
AUTO --> PUMPDOWN : Compressor status is 'PUMPDOWN'
AUTO --> PRE_OPEN : Compressor status is 'STOPPED'
PUMPDOWN : Gradually move to full closed position
PUMPDOWN --> PRE_OPEN : Compressor status is 'STOPPED'
}
ON --> OFF : Unit status is 'OFF'
ON --> INIT : EVD fault occurred
@enduml
@startuml Compressor Control SM Control SM
[*] --> OFF
OFF : Compressor is stopped.
OFF --> ON : Unit status is 'ON' and\nTsat is greater than setpoint and\nNo compressor fault
state ON {
[*] --> PRE_START
PRE_START : Waiting for EEV at pre-opened position
PRE_START --> AUTO : EEV is 'PRE_OPEN'
PRE_START --> OFF : Any compressor fault is detected
AUTO : PID control based on supply air temperature
AUTO --> PUMPDOWN : Compressor status is 'PUMPDOWN'
AUTO --> OFF : Any compressor fault is detected
PUMPDOWN : Set compressor speed a configurable constant
PUMPDOWN --> OFF : Low pressure is below threshold or\npump down timeout is expired
}
ON --> OFF : Unit status is 'OFF' or\nTsat is much lower than threshold or\nany compressor fault is detected
@enduml

## Modbus Register Map
Modicon Standard Register Number | Absolute Register Number (Hex) | Absolute Register Number (Dec) | Data Point | R/W | Length | Data Type | Scale | Units | Valid Response
System ID
|  |  | Model Number | R | 15 | ASCII
|  |  | Serial Number | R | 10 | ASCII
|  |  | Firmware Revision | R | 12 | ASCII
|  |  | BIOS Revision | R | 4 | ASCII
Unit Control (Metric)
|  |  | Unit | RW | 1 | ENUM |  |  | 0 = Off; 1 = On
|  |  | Startup Delay | RW | 1 | UINT16 | 0 | sec
|  |  | Cooling Strategy | RW | 1 | ENUM |  |  | 0 = RACS; 1 = HACS; 2 = INROW; 3 = CACS; 4 = Manual
|  |  | Supply Air Setpoint | RW | 1 | UINT16 | 1 | C
|  |  |  | RW | 1 | UINT16 | 1 | C
|  |  | Delta-T Setpoint | RW | 1 | ENUM |  |  | 0 = 10F/5.6C; 1 = 15F/8.3C; 2 = 20F/11.1C; 3 = 25F/13.9C; 4 = 30F/16.7C; 5 = 35F/19.4C; 6 = 40F/22.2C
|  |  | Maximum Fan Speed | RW | 1 | UINT16 | 1 | %
|  |  |  | RW | 1 | UINT16 | 1 | %
|  |  | Unit Role Override | RW | 1 | ENUM |  |  | 0 = Automatic; 1 = Forced On
|  |  | Idle on Leak Detect | RW | 1 | ENUM |  |  | 0 = No; 1 = Yes
|  |  | Shutdown Input State | R | 1 | ENUM |  |  | 0 = Open; 1 = Closed
|  |  | Shutdown Input Present | RW | 1 | ENUM |  |  | 0 = No; 1 = Yes
|  |  | Shutdown Input Normal State | RW | 1 | ENUM |  |  | 0 = Open; 1 = Closed
Unit Status (Metric)
|  |  | Mode | R | 1 | ENUM |  |  | 0 = Unknown; 1 = Initializing; 2 = Off; 3 = Standby; 4 = Idle; 5 = Startup Delay; 6 = Active; 7 = Maintenance
|  |  | Supply Temperature | R | 1 | INT16 | 1 | C
|  |  | Maximum Rack Inlet Temperature | R | 1 | INT16 | 1 | C
|  |  | Return Temperature | R | 1 | INT16 | 1 | C
|  |  | Room Temperature | R | 1 | INT16 | 1 | C
|  |  | Humidity | R | 1 | INT16 | 1 | %RH
|  |  | Dew Point Temperature | R | 1 | INT16 | 1 | C
|  |  | Airflow | R | 1 | UINT16 | 0 | L/s
|  |  | Air Filter Pressure | R | 1 | INT16 | 0 | Pa
|  |  | Cool Demand | R | 1 | UINT16 | 1 | kW
|  |  | Cool Output | R | 1 | UINT16 | 1 | kW
|  |  | Upper Supply Temperature | R | 1 | INT16 | 1 | C
|  |  | Lower Supply Temperature | R | 1 | INT16 | 1 | C
|  |  | Upper Return Temperature | R | 1 | INT16 | 1 | C
|  |  | Lower Return Temperature | R | 1 | INT16 | 1 | C
|  |  | Rack Inlet Temperature 1 | R | 1 | INT16 | 1 | C
|  |  | Rack Inlet Temperature 2 | R | 1 | INT16 | 1 | C
|  |  | Rack Inlet Temperature 3 | R | 1 | INT16 | 1 | C
|  |  | Rack Inlet Temperature 4 | R | 1 | INT16 | 1 | C
|  |  | Suction Pressure | R | 1 | UINT16 | 1 | bar
|  |  | Discharge Pressure | R | 1 | UINT16 | 1 | bar
|  |  | Suction Evap. Temp. | R | 1 | INT16 | 1 | C
|  |  | Discharge Cond. Temp. | R | 1 | INT16 | 1 | C
|  |  | Inlet Evap Coil Temperature | R | 1 | INT16 | 1 | C
|  |  | Outlet Evap Coil Temperature | R | 1 | INT16 | 1 | C
|  |  | Superheat | R | 1 | INT16 | 1 | C
|  |  | Fan 1 | R | 1 | UINT16 | 0 | rpm
|  |  | Fan 2 | R | 1 | UINT16 | 0 | rpm
|  |  | Fan 3 | R | 1 | UINT16 | 0 | rpm
|  |  | Fan 4 | R | 1 | UINT16 | 0 | rpm
|  |  | Fan 5 | R | 1 | UINT16 | 0 | rpm
|  |  | Fan 6 | R | 1 | UINT16 | 0 | rpm
|  |  | Fan 7 | R | 1 | UINT16 | 0 | rpm
|  |  | Fan 8 | R | 1 | UINT16 | 0 | rpm
|  |  | Compressor Speed | R | 1 | UINT16 | 1 | Hz
|  |  | EEV Position | R | 1 | UINT16 | 1 | %
|  |  | Condenser Fan Speed | R | 1 | UINT16 | 1 | %
|  |  | Power Feed Type | R | 1 | ENUM |  |  | 0 = Single; 1 = Dual
|  |  | Fan Power Supply 1 | R | 1 | UINT16 | 3 | A
|  |  | Fan Power Supply 2 | R | 1 | UINT16 | 3 | A
|  |  | Condenser Fan Power | R | 1 | UINT16 | 0 | W
|  |  | Compressor Power | R | 1 | UINT16 | 2 | kW
|  |  | Shutdown Input State | R | 1 | ENUM |  |  | 0 = Open; 1 = Closed
|  |  | Alarm Relay 1 | R | 1 | ENUM |  |  | 0 = Open; 1 = Closed
|  |  | Alarm Relay 2 | R | 1 | ENUM |  |  | 0 = Open; 1 = Closed
|  |  | Alarm Relay 3 | R | 1 | ENUM |  |  | 0 = Open; 1 = Closed
|  |  | Alarm Relay 4 | R | 1 | ENUM |  |  | 0 = Open; 1 = Closed
|  |  | Group Minimum Rack Temperature | R | 1 | INT16 | 1 | C
|  |  | Group Maximum Rack Temperature | R | 1 | INT16 | 1 | C
|  |  | Total Airflow | R | 1 | UINT16 | 0 | L/s
|  |  | Total Air Side Cooling Demand | R | 1 | UINT16 | 1 | kW
|  |  | Total Sensible Cooling Power | R | 1 | UINT16 | 1 | kW
|  |  | Active Flow Control Status | R | 1 | ENUM |  |  | 0 = Under; 1 = Okay; 2 = Over; 3 = NA; 4 = NA
|  |  | Unit | RW | 1 | ENUM |  |  | 0 = Off; 1 = On
|  |  | Startup Delay | RW | 1 | UINT16 | 0 | sec
|  |  | Cooling Strategy | RW | 1 | ENUM |  |  | 0 = RACS; 1 = HACS; 2 = INROW; 3 = CACS; 4 = Manual
|  |  | Supply Air Setpoint | RW | 1 | UINT16 | 1 | F
|  |  | Cool Setpoint | RW | 1 | UINT16 | 1 | F
|  |  | Delta-T Setpoint | RW | 1 | ENUM |  |  | 0 = 10F/5.6C; 1 = 15F/8.3C; 2 = 20F/11.1C; 3 = 25F/13.9C; 4 = 30F/16.7C; 5 = 35F/19.4C; 6 = 40F/22.2C
|  |  | Maximum Fan Speed | RW | 1 | UINT16 | 1 | %
|  |  | Manual IT Fan Speed | RW | 1 | UINT16 | 1 | %
|  |  | Unit Role Override | RW | 1 | ENUM |  |  | 0 = Automatic; 1 = Forced On
|  |  | Idle on Leak Detect | RW | 1 | ENUM |  |  | 0 = No; 1 = Yes
|  |  | Shutdown Input State | R | 1 | ENUM |  |  | 0 = Open; 1 = Closed
|  |  | Shutdown Input Present | RW | 1 | ENUM |  |  | 0 = No; 1 = Yes
|  |  | Shutdown Input Normal State | RW | 1 | ENUM |  |  | 0 = Open; 1 = Closed
|  |  | Protect On/Standby | RW | 1 | ENUM |  |  | 0 = Disable; 1 = Enable
|  |  | Runtime Balancing Difference | RW | 1 | UINT16 | 0 | hr
|  |  | Switchover Handoff Time | RW | 1 | UINT16 | 0 | min
|  |  | Mode | R | 1 | ENUM |  |  | 0 = Unknown; 1 = Initializing; 2 = Off; 3 = Standby; 4 = Idle; 5 = Startup Delay; 6 = Active; 7 = Maintenance
|  |  | Supply Temperature | R | 1 | INT16 | 1 | F
|  |  | Maximum Rack Inlet Temperature | R | 1 | INT16 | 1 | F
|  |  | Return Temperature | R | 1 | INT16 | 1 | F
|  |  | Room Temperature | R | 1 | INT16 | 1 | F
|  |  | Humidity | R | 1 | INT16 | 1 | %RH
|  |  | Dew Point Temperature | R | 1 | INT16 | 1 | F
|  |  | Airflow | R | 1 | UINT16 | 0 | CFM
|  |  | Air Filter Pressure | R | 1 | INT16 | 2 | inWC
|  |  | Cool Demand | R | 1 | UINT16 | 1 | kW
|  |  | Cool Output | R | 1 | UINT16 | 1 | kW
|  |  | Upper Supply Temperature | R | 1 | INT16 | 1 | F
|  |  | Lower Supply Temperature | R | 1 | INT16 | 1 | F
|  |  | Upper Return Temperature | R | 1 | INT16 | 1 | F
|  |  | Lower Return Temperature | R | 1 | INT16 | 1 | F
|  |  | Rack Inlet Temperature 1 | R | 1 | INT16 | 1 | F
|  |  | Rack Inlet Temperature 2 | R | 1 | INT16 | 1 | F
|  |  | Rack Inlet Temperature 3 | R | 1 | INT16 | 1 | F
|  |  | Rack Inlet Temperature 4 | R | 1 | INT16 | 1 | F
|  |  | Suction Pressure | R | 1 | UINT16 | 1 | psi
|  |  | Discharge Pressure | R | 1 | UINT16 | 1 | psi
|  |  | Suction Evap. Temp. | R | 1 | INT16 | 1 | F
|  |  | Discharge Cond. Temp. | R | 1 | INT16 | 1 | F
|  |  | Inlet Evap Coil Temperature | R | 1 | INT16 | 1 | F
|  |  | Outlet Evap Coil Temperature | R | 1 | INT16 | 1 | F
|  |  | Superheat | R | 1 | INT16 | 1 | F
|  |  | Fan 1 | R | 1 | UINT16 | 0 | rpm
|  |  | Fan 2 | R | 1 | UINT16 | 0 | rpm
|  |  | Fan 3 | R | 1 | UINT16 | 0 | rpm
|  |  | Fan 4 | R | 1 | UINT16 | 0 | rpm
|  |  | Fan 5 | R | 1 | UINT16 | 0 | rpm
|  |  | Fan 6 | R | 1 | UINT16 | 0 | rpm
|  |  | Fan 7 | R | 1 | UINT16 | 0 | rpm
|  |  | Fan 8 | R | 1 | UINT16 | 0 | rpm
|  |  | Compressor Speed | R | 1 | UINT16 | 1 | Hz
|  |  | EEV Position | R | 1 | UINT16 | 1 | %
|  |  | Condenser Fan Speed | R | 1 | UINT16 | 1 | %
|  |  | Power Feed Type | R | 1 | ENUM |  |  | 0 = Single; 1 = Dual
|  |  | Fan Power Supply 1 | R | 1 | UINT16 | 3 | A
|  |  | Fan Power Supply 2 | R | 1 | UINT16 | 3 | A
|  |  | Condenser Fan Power | R | 1 | UINT16 | 0 | W
|  |  | Compressor Power | R | 1 | UINT16 | 2 | kW
|  |  | Shutdown Input State | R | 1 | ENUM |  |  | 0 = Open; 1 = Closed
|  |  | Alarm Relay 1 | R | 1 | ENUM |  |  | 0 = Open; 1 = Closed
|  |  | Alarm Relay 2 | R | 1 | ENUM |  |  | 0 = Open; 1 = Closed
|  |  | Alarm Relay 3 | R | 1 | ENUM |  |  | 0 = Open; 1 = Closed
|  |  | Alarm Relay 4 | R | 1 | ENUM |  |  | 0 = Open; 1 = Closed
Group Status (US Customary)
|  |  | Group Minimum Rack Temperature | R | 1 | INT16 | 1 | F
|  |  | Group Maximum Rack Temperature | R | 1 | INT16 | 1 | F
|  |  | Total Airflow | R | 1 | UINT16 | 0 | CFM
|  |  | Total Air Side Cooling Demand | R | 1 | UINT16 | 1 | kW
|  |  | Total Sensible Cooling Power | R | 1 | UINT16 | 1 | kW
|  |  | Active Flow Control Status | R | 1 | ENUM |  |  | 0 = Under; 1 = Okay; 2 = Over; 3 = NA; 4 = NA
Run Hours
|  |  | Unit Run Hours | R | 2 | UINT32 | 0 | hr
|  |  | Air Filter Run Hours | R | 2 | UINT32 | 0 | hr
|  |  | Compressor Run Hours | R | 2 | UINT32 | 0 | hr
|  |  | Condenser Fan Run Hours | R | 2 | UINT32 | 0 | hr
|  |  | Condensate Pump Run Hours | R | 2 | UINT32 | 0 | hr
|  |  | Fan 1 Run Hours | R | 2 | UINT32 | 0 | hr
|  |  | Fan 2 Run Hours | R | 2 | UINT32 | 0 | hr
|  |  | Fan 3 Run Hours | R | 2 | UINT32 | 0 | hr
|  |  | Fan 4 Run Hours | R | 2 | UINT32 | 0 | hr
|  |  | Fan 5 Run Hours | R | 2 | UINT32 | 0 | hr
|  |  | Fan 6 Run Hours | R | 2 | UINT32 | 0 | hr
|  |  | Fan 7 Run Hours | R | 2 | UINT32 | 0 | hr
|  |  | Fan 8 Run Hours | R | 2 | UINT32 | 0 | hr
Alarms
|  |  | Unexpected Number of Units in Group | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | Primary Power Source | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | Secondary Power Source | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | Output Relay 1 | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | Output Relay 2 | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | Output Relay 3 | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | Output Relay 4 | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | AFC Firmware Incompatiblity Detected | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | PIC 1 Firmware Incompatiblity Detected | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | PIC 2 Firmware Incompatiblity Detected | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | VFD Communication Error | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | VFD Drive Initialization Error | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | High Head Pressure | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | VFD Persistent Trips | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | VFD Power Card Temperature | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | VFD Earth Fault | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | VFD Control Card Over Temperature | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | VFD Peak Over Current | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | VFD Torque Limit Exceeded | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | VFD Motor Thermistor Over Temperature | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | VFD Motor Over Temperature | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | VFD Current Overload | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | VFD DC Overvoltage | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | VFD Short Circuit | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | VFD Inrush Error | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | VFD Mains Phase Loss | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | VFD Internal Error | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | VFD Motor Phase U Missing | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | VFD Motor Phase V Missing | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | VFD Motor Phase W Missing | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | VFD Vd D1 Supply Low | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | VFD Drive Initialized to Defaults | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | VFD Control Card Over Temperature Warning | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | VFD Current Overload Warning | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | VFD Undervoltage Warning | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | VFD DC Overvoltage Warning | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | VFD DC Link Voltage Low | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | VFD DC Link Voltage High | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | VFD Speed Not Within Limits | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | VFD Control Voltage Overloaded | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | VFD Current Limit Exceeded | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | Condenser Communication Error | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | Condenser Fan Mains Over Voltage | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | Condenser Fan Mains Under Voltage | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | Condenser Fan DC Link Under Voltage | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | Condenser Fan DC Link Over Voltage | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | Condenser Fan Electronic Over Heated | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | Condenser Fan Locked Motor | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | Condenser Fan Hall Sensor Error | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | Condenser Fan Motor Overheated | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | Condenser Fan Bad | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | Condenser Fan Communication Error | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | Condenser Fan Power Module Overheated | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | Condenser Fan Phase Error | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | Condenser Fan Cable Break | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | Condenser Fan Low Speed | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | Condenser Fan Brake Operation | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | Condenser Fan DC Link Voltage Low | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | Condenser Fan Electronics Temperature High | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | Condenser Fan Motor Temperature High | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | Condenser Fan Output Stage Temperature High | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | Condenser Fan Power Limitation | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | Condenser Fan Line Impedance Too High | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | Condenser Fan Current Limitation | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | Upper Return Temperature Sensor Error | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | Lower Return Temperature Sensor Error | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | Upper Supply Temperature Sensor Error | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | Lower Supply Temperature Sensor Error | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | Outlet Evap Coil Temperature Sensor Error | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | Inlet Evap Coil Temperature Sensor Error | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | Room Humidity Sensor Error Detected | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | Suction Pressure Sensor Error | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | Discharge Pressure Sensor Error | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | Air Filter Pressure Sensor Error | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | Unexpected Number of Rack Inlet Temperature Sensors Present | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | Rack inlet temperature sensor error detected | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | Unexpected Number of Leak Detectors Present | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | Leak Detected | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | Condensate Pan Full | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | Condensate Pan Warning | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | Condensate Lower Float Error | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | Condensate Pump Error | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | Fan 1 Error Detected | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | Fan 2 Error Detected | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | Fan 3 Error Detected | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | Fan 4 Error Detected | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | Fan 5 Error Detected | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | Fan 6 Error Detected | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | Fan 7 Error Detected | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | Fan 8 Error Detected | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | Input Voltage Not Configured | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | Suction Pressure Too Low To Start | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | Evap Coil Freeze Protection | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | Low Suction Pressure | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | High Head Pressure | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | Low Superheat | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | High Superheat | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | Persistent Low Suction Pressure | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | Persistent High Head Pressure | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | Persistent High/Low Superheat | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | Idle Due to Error | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | High Supply Temperature | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | High Return Temperature | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | Rack Inlet High Temperature | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | Low Humidity Threshold Exceeded | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | High Humidity Threshold Exceeded | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | Unit Run Hours Exceeded | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | Air Filter Run Hours Exceeded | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | EcoAisle Door Open | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | Unexpected Number of Active Flow Controllers | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | Insufficient Airflow | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | Active Flow Controller Sensor Error | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | Excessive Compressor Cycling Condition | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | Off Due to Input Contact | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | Smoke Detected | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | Air Filter Clogged | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | No Backup Units Available | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | EXV Error | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | Evaporator Fan Power Supply 1 Error Detected | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | Evaporator Fan Power Supply 2 Error Detected | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
|  |  | Evaporator Fan Power Supply Error Detected | R | 1 | ENUM |  |  | 0 = Inactive; 1 = Active
Modbus Counters
|  |  | CRC Errors | R | 2 | UINT32 | 0
|  |  | RX Packets | R | 2 | UINT32 | 0
|  |  | TX Packets | R | 2 | UINT32 | 0
|  |  | Frame Errors | R | 2 | UINT32 | 0
|  |  | Overrun Errors | R | 2 | UINT32 | 0
|  |  | Parity Errors | R | 2 | UINT32 | 0
|  |  | Rx 1.5 Errors | R | 2 | UINT32 | 0
|  |  | Rx 3.5 Errors | R | 2 | UINT32 | 0
|  |  | Baud Rate | R | 2 | UINT32 | 0

## Verification Tracking (hidden)
|  | Open | Close | Fixed | As Design
| DOC | 0 | 0 | 0 | 0
| GUI | 0 | 0 | 0 | 0
| SW | 0 | 0 | 0 | 0
| Sub Total | 0 | 0 | 0 | 0
| Total | 0
NO. | Issue Description | Category | Found Version | Repaired Version | Last Date | Status | Comment

## Settings (hidden)
Priorities | Status | Notifications | Level
- | - | - | - | Using This Worksheet
High | Planning | SP says: RAR | Must | These lists are used to populate the drop-down boxes
Med | Pending Approval | SP says: FYI | Optional | in the Projects worksheet. You can edit these lists as
Low | Approved | SP says: NTD | Nice to have | needed. For example, it may be more convenient to
Done | In Progress | C says: RAR | Deprecated | use names in place of "SP" (for service provider) and
| Pending Review | C says: FYI |  | "C" (for client).
| On Hold | C says: NTD
| Completed |  |  | For information about how these lists are used to
populate the drop-down boxes, see the following article:
http://www.vertex42.com/ExcelTips/drop-down-list.html
Fixed
Open
Close
As Design